| Parameter | Preliminary value | Basis / limitation |
| --- | --- | --- |
| Canal length | 100 m | Assumed from project description |
| Canal width | 25 m | Assumed clear width to be covered; confirm by survey |
| Gross canopy footprint | 2,500 m² | 100 m × 25 m |
| Illustrative module rating | 625 Wp | Example model appears in SREDA approved-module list |
| Illustrative module area | 2.70 m² | Approximation for layout calculation; replace with selected datasheet |
| Usable module footprint | 70–80% of gross area | Planning allowance only; not an engineering standard |
| PV resource | 3.68–4.23 kWh/kWp/day | Bangladesh-wide Global Solar Atlas range; site-specific output may differ |
| Grid arrangement | Grid-connected, subject to approval | Requires utility study, protection, metering and applicable rules |

| Brand / model | Listed power | Evidence in official listing |
| --- | --- | --- |
| LONGi LR8-66HGD-625M | 625 Wp | SREDA database lists model and BDS IEC module safety/performance standards |
| Trina Solar TSM-630NEG19RC.70 | 630 Wp | SREDA database listing |
| Jinko Solar JKM630N-78HL4BDV | 630 Wp | SREDA database listing |
| Jinko Solar JKM720N-66HL5-BDV | 720 Wp | SREDA database listing |

| Case | Usable area | Approx. module count | DC capacity | Meaning |
| --- | --- | --- | --- | --- |
| Lower layout case | 1,750 m² | 648 | 405 kWp | More space reserved for gaps/access |
| Upper layout case | 2,000 m² | 740 | 462.5 kWp | Denser layout; only if structural/access layout permits |

| Installed DC capacity | At 3.68 kWh/kWp/day | At 4.23 kWh/kWp/day | 30-day range | Annual range (365 d) |
| --- | --- | --- | --- | --- |
| 405 kWp | 1,490 kWh/day | 1,713 kWh/day | 44.7–51.4 MWh | 544.0–625.3 MWh |
| 462.5 kWp | 1,702 kWh/day | 1,956 kWh/day | 51.1–58.7 MWh | 621.2–714.1 MWh |

| Potential benefits | Risks and conditions |
| --- | --- |
| Renewable electricity for pumping and farm operations. | Output varies with season, cloud, temperature, dust and shading. |
| May reduce direct sunlight and evaporation from covered water surfaces. | Evaporation reduction is site-specific and should be measured or modelled. |
| Uses overhead space rather than directly occupying more crop land. | Canopy supports, access routes and foundations still use land and may constrain maintenance. |
| Surplus power may have economic value if grid export is approved. | Export limits, tariffs, grid capacity and metering rules may affect economics. |
| Potential reduction in diesel use where solar replaces diesel pumping. | Embodied emissions, module end-of-life handling and structural materials should be included in lifecycle planning. |

Appendix A. Calculation Summary

Gross canopy footprint = 100 × 25 = 2,500 m².

Assumed module footprint = 2.70 m²; assumed usable fraction = 0.70–0.80.

Module count = (2,500 × 0.70 to 2,500 × 0.80) ÷ 2.70 ≈ 648–740 modules.

DC capacity = module count × 0.625 kW ≈ 405–462.5 kWp.

Daily energy screen = capacity (kWp) × PVOUT (kWh/kWp/day), using 3.68–4.23.

Daily energy screen ≈ 405 × 3.68 to 462.5 × 4.23 = 1,490–1,956 kWh/day.

Monthly energy screen = daily energy × 30 ≈ 44.7–58.7 MWh per 30-day month.

| Parameter | Calculated value |
| --- | --- |
| Motor rating | 5 HP |
| Mechanical output | 3.73 kW |
| Assumed motor efficiency | 85–90% |
| Electrical input power | 4.15–4.39 kW |
| Electricity used in 1 hour | 4.15–4.39 kWh |
| Electricity used in 8 hours | 33.2–35.1 kWh |
| Electricity used in 30 days, at 8 h/day | 995–1,053 kWh |
| Electricity used in 1 year, at 8 h/day | 12.1–12.8 MWh |

For an 8-hour motor operating schedule:

E {export} =E {solar} - E {motor} - E {other loads} –  E {losses not already counted}

| Energy calculation | Lower estimate | Higher estimate |
| --- | --- | --- |
| Solar electricity generated per day | 1,490 kWh | 1,956 kWh |
| Motor consumption per day (8 hours) | 35 kWh | 33 kWh |
| Potential surplus per day | 1,455 kWh | 1,923 kWh |
| Potential surplus in 30 days | 43,650 kWh | 57,690 kWh |
| Solar generation per year | 544 MWh | 714 MWh |
| Motor consumption per year | 12.8 MWh | 12.1 MWh |
| Potential surplus per year | 531 MWh | 702 MWh |

How much carbon emission can the project avoid?

To estimate the potential emission reduction, we need a grid emission factor. A Bangladesh Department of Environment communication dated January 2025 reported the country's grid emission factor as:

- 0.61 tonnes of CO₂ per MWh for 2019–20.

- 0.62 tonnes of CO₂ per MWh for 2020–21 and 2021–22.

- For a preliminary estimate, we use 0.62 tCO₂/MWh:

- Estimated avoided emissions = Electricity displacing grid generation × 0.62

Main equation for carbon credits

Carbon Credits (tCO₂e) = Baseline Emissions - {Project Emissions}

For your project, a simplified equation is:

CC = E {export} × EF {grid} - PE

Where:

- CC = Net carbon credits earned (tCO₂e)

- E {export} = Net electricity exported to the national grid (MWh)

- EF {grid} = Applicable grid emission factor (tCO₂e/MWh)

- PE = Project emissions, including applicable fuel use and other sources (tCO₂e)

2. Calculate carbon credits from solar electricity

If your project generates electricity from solar panels installed over an irrigation canal, the potential avoided emissions are:

ER = E {solar,displaced} × EF {grid}

Here, E {solar,displaced} is the amount of electricity that actually displaces grid electricity, rather than simply the total electricity generated.

For example, assume:

- Net electricity exported = 100 MWh/year

- Illustrative grid emission factor = 0.50 tCO₂e/MWh

- Project emissions = 0 tCO₂e/year for simplicity

Then:

ER=100 × 0.50

ER=50 tCO₂e/year

| Calculation | Lower estimate | Higher estimate |
| --- | --- | --- |
| Annual solar generation | 544 MWh | 714 MWh |
| Illustrative grid emission factor | 0.62 tCO₂/MWh | 0.62 tCO₂/MWh |
| Estimated avoided emissions per year | 337 tCO₂ | 443 tCO₂ |

| Indicator | Preliminary result |
| --- | --- |
| Irrigation motor | 5 HP |
| Assumed motor operation | 8 hours/day |
| Daily motor electricity consumption | 33–35 kWh |
| Solar plant capacity | 405–463 kWp |
| Potential daily surplus | 1,455–1,923 kWh |
| Potential annual grid export | 531–702 MWh |
| Annual avoided emissions, including qualifying self-consumption | 337–443 tCO₂ |
| Potential annual reduction associated with grid exports alone | 329–435 tCO₂ |

References

Sustainable and Renewable Energy Development Authority (SREDA). (n.d.). List of approved solar modules for net metering program. Government of Bangladesh. https://nsrra.sreda.gov.bd/solar/nem/smodule/index.php?pg=1

Power Division, Ministry of Power, Energy and Mineral Resources, Government of Bangladesh. (2025). Net Metering Guideline–2025. https://powerdivision.gov.bd/pages/files/6948fac3559d93a15090eea0

Sustainable and Renewable Energy Development Authority (SREDA), Power Division, Ministry of Power, Energy and Mineral Resources. (2020). Guidelines for grid integration of solar irrigation pump (approved 26 July 2020). https://solar.iwmi.org/wp-content/uploads/sites/43/2023/05/Guideline-of-Solar-Irrigation-Pump-Grid-Integration_English.pdf

de Oliveira, G., et al. (2024). PV to reduce evaporative losses in the channels of the São Francisco’s River water transposition project. (Open-access research article). https://pmc.ncbi.nlm.nih.gov/articles/PMC10954660/

https://www.scribd.com/document/856423066/Grid-Emission-Factor-GEF-for-Bangladesh-23-01-2025